## gen_tech_
Tech | InvCost | FuelCost | FixOM | VarOM | Efficiency | Alpha | Carrier | Lifetime | HeatType | LoadFactor | MinLoad | StartTime | StartCost | StartFuel | StartFuelType | PartLoadCost | StartCO2 | PartLoadCO2 | CO2_factor | Space_m2 | Abbr_name | DEA_name | Techprop_name
COCHP | 2.0128 | 35.86 | 0.032911 | 3.08e-06 | 0.54 | 0.15 | EL, HEAT | 25 |  | 0.85 | 0.3 | 12 | 5.69e-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1000 | Coal CHP | 01 Coal CHP | H_meanalpha_CHP
GTSC | 0.55295 | 54.81 | 0.019141 | 4.25e-06 | 0.43 | 0 | EL | 25 |  | 0.85 | 0.2 | 0.5 | 2.02e-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1000 | Gas Turbine Simple Cycle | 04 Gas turb. simple cycle, L | G_peak
CCGT | 0.8507 | 54.81 | 0.027648 | 4.2535e-06 | 0.63 | 0.15 | EL, HEAT | 25 |  | 0.85 | 0.4 | 2 | 4.29e-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1000 | Combined Cycle Gas Turbine | 05 Gas turb. CC, steam extract. | G
GEBG | 0.90387 | 54.81 | 0.0090387 | 6.3802e-06 | 0.47 | 0 | EL | 25 |  | 0.85 | 0.5 | 0.3 | 2.02e-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1000 | Gas Engine Biogas | 06 Gas engines, biogas | WG_peak
WCHP | 7.518 | 17.6 | 0.17227 | 2.7159e-05 | 0.22 | 0.3 | EL, HEAT | 25 |  | 0.85 | 0.2 | 2 | 5.69e-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1000 | Waste CHP | 08 WtE CHP, Large, 50 degree | WA_lowalpha_CHP
WBO | 1.6376 | 17.6 | 0.0688 | 9.0068e-06 | 1.06 | 1 | HEAT | 25 |  | 0.85 | 0.7 | 12 | 5.69e-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1000 | Waste Boiler | 08 WtE HOP
WCCHP | 2.4458 | 24 | 0.065929 | 2.8711e-06 | 0.39 | 0.4 | EL, HEAT | 25 |  | 0.85 | 0.45 | 12 | 5.69e-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1000 | Wood Chips Biomass CHP | 09a Wood Chips extract. Plant | W_lowalpha_CHP
WPCHP | 2.0204 | 61.18 | 0.052105 | 1.1697e-06 | 0.43 | 0.52 | EL, HEAT | 25 |  | 0.85 | 0.15 | 12 | 5.69e-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1000 | Wood Pellets Biomass CHP | 09b Wood Pellets extract. Plant | W_lowalpha_CHP
SBCHP | 3.3071 | 21.7 | 0.11591 | 2.2756e-06 | 0.28 | 0.43 | EL, HEAT | 25 |  | 0.85 | 0.4 | 8 | 5.69e-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1000 | Straw Biomass CHP | 09c Straw, Large, 50 degree | W_lowalpha_CHP
SOFC | 0.8507 | 1 | 0.042535 | 0 | 0.6 | 0 | EL, H2 | 20 |  | 0.85 | 0.7 | 25 | 0 | [5 empty] | 1 | 1000 | Solid Oxide Fuel Cell | 11 SOFC-CHP | FC
PFC | 0.8507 | 1 | 0.042535 | 0 | 0.5 | 0 | EL, H2 | 10 |  | 0.85 | 0.1 | 0 | 0 | [5 empty] | 1 | 1000 | Low Temp PEM Fuel Cell | 12 LT-PEMFC CHP | FC
WON | 1.0903 | 0 | 0.015602 | 1.8495e-06 | 1 | 0 | EL | 30 |  | 0.85 | 0 | 0 | 0 | [5 empty] | 0 | 1000 | Wind Onshore | 20 Onshore turbines | WON
WOFF | 1.64 | 0 | 0.033 | 3.25e-06 | 1 | 0 | EL | 30 |  | 0.85 | 0 | 0 | 0 | [5 empty] | 0 | 1000 | Wind Offshore | 21 Offshore turbines | WOFF
PVROOF | 0.64 | 0 | 0.0089 | 0 | 1 | 0 | EL | 40 |  | 0.85 | 0 | 0 | 0 | [5 empty] | 0 | 1000 | PV Rooftop | 22 Rooftop PV residential | PV
PVUTIL | 0.29 | 0 | 0.0074 | 0 | 1 | 0 | EL | 40 |  | 0.85 | 0 | 0 | 0 | [5 empty] | 0 | 1000 | Fixed Axis Utility Scale PV | 22 Utility-scale PV | PV
PVTRACK | 0.35 | 0 | 0.009 | 0 | 1 | 0 | EL | 40 |  | 0.85 | 0 | 0 | 0 | [5 empty] | 0 | 1000 | Single Axis Tracking Utility PV | 22 Utility-scale PV tracker | PVOPT
HPAIR | 0.80816 | 1 | 0.0021267 | 1.7971e-06 | 3.9 | 3.9 | HEAT | 25 |  | 0.85 | 0.25 | 1 | 0 | [5 empty] | 0 | 1000 | Heat Pumps Air Source | 40 Comp. hp, airsource 10 MW | HP
HPEX | 0.60612 | 1 | 0.0021267 | 1.7971e-06 | 5.5 | 5.5 | HEAT | 25 |  | 0.85 | 0.25 | 1 | 1.063e-05 | [5 empty] | 0 | 1000 | Heat Pumps Excess Heat | 40 Comp. hp, excess heat 10 MW | HP
EB | 0.063802 | 1 | 0.0009783 | 1.0634e-06 | 0.99 | 0.99 | HEAT | 25 |  | 0.85 | 0.05 | 0.1 | 0 | [5 empty] | 0 | 1000 | Electric Boiler | 41 Electric boiler, large | EB
GB | 0.053169 | 54.81 | 0.0018077 | 1.0634e-06 | 1.04 | 1.04 | HEAT | 25 |  | 0.85 | 0.15 | 0.4 | 0 | [5 empty] | 0 | 1000 | Natural Gas Boiler | 44 Natural Gas DH Only
AEC | 0.275 | 1 | 0.04 | 0 | 0.699 | 0 | H2 | 25 |  | 0.85 | [8 empty] | 0 | 1000 | Alkaline Electrolyser | 86 AEC 1 GW | electrolyser
PEMEC | 0.325 | 1 | 0.02 | 0 | 0.664 | 0 | H2 | 25 |  | 0.85 | [8 empty] | 0 | 1000 | PEMEC Electrolyser | 86 PEMEC 1 GW | electrolyser
HYD | 999999 | 0 | 0.0085072 | 0 | 0.99 | 0 | EL | 50 |  | 0.85 | [8 empty] | 0 | 1000 | Hydropower
Note on G1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Cb/Cv, here means the percentage of heat acquired, e.g. 0.15 means 85% el, 15% heat
Note on K1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assumptions
Note on L1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: % of rating
Note on M1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hours
Note on O1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not relevant for now?
Note on P1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not relevant for now?
Note on Q1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Maybe not used for now?
Note on W1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Name according to DEA tech data
Note on X1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Name refer to group tech prop file
Note on D22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: % of specific investment
Note on D23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: % of specific investment

## remarks
use 2050 ctrl scenario
financial data converted into M€/MW units from DEA datasheet
DEA data takes precedence, if not found, use techprop data
Starttime considers cold start time
Assume 50 degrees for DH heating generations
Hydropower is hypothetical data because most probably will not be invested in the future, but operating the exisitng ones is possible